## Cover
SOLAR PV SYSTEM INSTALLATION COMMISSIONING REPORT
Regen Renewables (Pvt) Ltd. · 31/10 Castle Street, Colombo 8, Sri Lanka · regen.lk
1. GENERAL DETAILS
Project Name |  | Document No.
Address |  | Revision No. | Rev 0
Contact Person Name |  | Commissioning Date
Telephone — Fixed |  | Telephone — Mobile
E-Mail |  | Weather Condition
Electricity Bill Available |  | Client
2. PV SYSTEM & UTILITY DETAILS
EPC / Installation Contractor |  | Inverter Brand & Model
PV System Capacity (kWp) |  | Number of Inverters
System AC Capacity (kW) |  | Roof Structure
PV System Connection Method |  | Utility System Voltage
Utility Supplier |  | Utility Supplier's Branch Office
Utility Account No. |  | Installation Type
3. PV PANEL DETAILS
PV Module Brand & Model |  | Rated Power (Wp)
Voc / Vmp (V) |  | Imp / Isc (A)
Number of Panels |  | Number of Strings
4. PREPARED / REVIEWED / APPROVED
Prepared By (Name / Company) |  | Reviewed By (Name / Company)
Approved By (Name / Company) |  | Approval Date
5. HOW THIS WORKBOOK WORKS
• Yellow cells = fill in on site. Grey cells = calculated automatically (Pass / Fail, totals, deviations) — do not type over them.
• Every reading is entered ONCE, in its own table. The Summary sheet collects all results automatically, and the project name is picked up from this Cover on every sheet.
• Acceptance limits (minimum insulation, earth resistance, voltage / frequency window, thermal ΔT) are on “Equipment and Limits”. They are defaults — edit them to your company / utility standard.
• Inverters differ per project: copy the “DC INV 01” tab (right-click → Move or Copy → Create a copy), rename it, then add a matching row on the Summary sheet. MPPT / String columns are free-text, so any layout works.
• Insulation testers that show “>” or “OL”: type the highest number displayed (e.g. 999). Single-phase inverters: type N/A in the L2 / L3 insulation cells.
• Battery Test applies to hybrid systems only — set “Applicable” to Yes on the Summary sheet when a battery is installed.
6. REPORT CONTENTS
1 | Summary (auto)
2 | Equipment and Limits
3 | Visual Inspection
4 | Inverters and Panel
5 | DC String Tests — one sheet per inverter
6 | AC Output (incl. grid no-load)
7 | AC Insulation and Earthing
8 | Thermal Imaging
9 | Battery (hybrid only)
10 | Protection and Grid
11 | Punch List
12 | Sign-Off & Handover

## Summary
COMMISSIONING SUMMARY (calculated automatically)
Project
Commissioning Date
No. | Section | Applicable | Pass | Fail | Open | Status | Remarks
1 | Visual & Mechanical Inspection | Yes
2 | DC String Tests — INV 01 | Yes
3 | DC String Tests — INV 02 | Yes
4 | AC Output (grid no-load & inverters) | Yes
5 | AC Insulation Resistance | Yes
6 | Earthing | Yes
7 | Thermal Imaging (panels, inverters, switchgear) | Yes
8 | Battery Test (hybrid systems only) | No
9 | Protection & Grid Settings | Yes
10 | Punch List — all items closed | Yes
OVERALL RESULT
Added another inverter? Copy a DC sheet, then insert a row here and point it at the new sheet’s Result column (column N, rows 15–50).

## Equipment and Limits
TEST EQUIPMENT & ACCEPTANCE LIMITS
TEST EQUIPMENT REGISTER — recorded once, applies to every test in this report
No. | Instrument | Model / Make | Serial No. | Calibrated On | Calibration Due | Used For
1 | Insulation Resistance Tester |  |  |  |  | DC & AC insulation tests
2 | Digital Multimeter / Clamp Meter |  |  |  |  | Voltage, current, polarity
3 | PV String Tester / I-V Curve Tracer |  |  |  |  | Voc, Isc, string current
4 | Digital Earth Tester | 4105A / KYORITSU |  |  |  | Earthing test
5 | Thermal Imaging Camera |  |  |  |  | Panels, inverters, switchgear
6 | Power / Energy Analyser |  |  |  |  | AC output, PF, frequency
7 | Irradiance Meter |  |  |  |  | Irradiance during on-load tests
8 | Other
ACCEPTANCE LIMITS — defaults, edit to match your company / utility standard
No. | Parameter | Value | Unit | Used in
1 | DC insulation resistance — minimum | 1 | MΩ | DC String Tests
2 | AC insulation resistance — minimum | 1 | MΩ | AC Insulation and Earthing
3 | String Voc deviation within same MPPT / module count — maximum | 5% | % | DC String Tests
4 | Earth resistance — maximum | 5 | Ω | AC Insulation and Earthing
5 | Nominal phase voltage (L–N) | 230 | V | AC Output
6 | Voltage tolerance (±) | 10% | % | AC Output
7 | Nominal frequency | 50 | Hz | AC Output
8 | Frequency tolerance (±) | 1 | Hz | AC Output
9 | Thermal ΔT above ambient — maximum | 20 | °C | Thermal Imaging

## Visual Inspection
VISUAL & MECHANICAL INSPECTION CHECKLIST
No. | Inspection Item | Status | Remarks
A. PV Modules & Mounting Structure
1 | Modules free of physical damage (cracks, hot spots, delamination)
2 | Modules clean and free of shading obstructions
3 | Mounting structure secure, level and correctly torqued
4 | Module clamps / bolts torqued to spec, no loose fixings
5 | Structure and module frames bonded to earthing system
B. DC Cabling
6 | DC cables routed and dressed neatly, no sharp bends
7 | Cables secured with UV-rated cable ties / clips
8 | MC4 (or equivalent) connectors fully locked, no exposed conductor
9 | String / cable labelling complete and legible
10 | Cable entry points and conduits sealed (IP rated)
C. Inverter & DC Protection
11 | Inverter securely mounted, correct orientation and clearance
12 | Ventilation / cooling clearance around inverter as per manual
13 | Cable glands sealed, unused entries blanked off
14 | DC surge protection device (SPD) fitted and indicator normal
15 | DC isolator / switch labelled and operates freely
16 | Inverter display / status LEDs functioning normally
D. AC Side & Main Panel
17 | AC cable terminations tight and correctly torqued
18 | AC circuit breaker rating matches design / datasheet
19 | AC isolator accessible and labelled
20 | AC cable and circuit labelling complete
21 | Energy meter / CT connections correct and secure
E. Earthing & Lightning Protection
22 | Earth pit(s) installed and accessible for testing
23 | Earth cable size / type as per design
24 | Equipotential bonding complete across all metallic parts
25 | Lightning / surge protection installed where specified
F. Safety & Signage
26 | Danger / warning labels posted at DC & AC points
27 | Single line diagram (SLD) posted at site / inverter room
28 | Fire extinguisher (CO2 / DCP, rated for electrical) available
29 | PPE available for O&M personnel
30 | Emergency shutdown procedure posted
Inspected By
Date

## Inverters and Panel
INVERTER REGISTER & MAIN PANEL DETAILS
INVERTER REGISTER — one row per inverter (strings / PV modules per inverter are totalled on each DC String Test sheet)
No. | Location / Room | Make | Model | Serial No. | Rated Power (kW) | DC SPD (Y/N) | DC SPD Model | DC Isolator Qty | DC Isolator Rating | DC Cable (size / type) | AC Isolator (Y/N) | AC Isolator Rating | Remarks
1
2
3
4
5
6
7
8
9
10
MAIN ELECTRICAL PANEL & CABLE DETAILS
Main panel location | [5 empty] | Energy meter serial no.
Main breaker make / model | [5 empty] | CT ratio (if used)
Main breaker rating (A) | [5 empty] | RCD / ELCB rating (mA)
Enclosure IP rating | [5 empty] | AC cable: inverter → panel (size / type / length)
AC SPD fitted (Y/N) | [5 empty] | AC cable: panel → utility (size / type / length)
Energy meter make / model | [5 empty] | Earth conductor size

## DC INV 01
DC STRING TEST — INV 01
INVERTER DETAILS
Inverter No. |  |  |  | INV 01 |  |  | Inverter Location / Room
Make / Model | [6 empty] | Serial No.
Rated Capacity (kW) | [6 empty] | Date / Time
Tested By | [6 empty] | Weather / Irradiance (W/m²)
Total Strings Listed | [6 empty] | Total PV Modules
STRING TESTS — each string is entered ONCE (MPPT / string / module count are not repeated)
STRING DETAILS |  |  |  | NO-LOAD (before energising) | [5 empty] | ON-LOAD |  | RESULT
No. | MPPT | String | PV Modules | Voc (V) | Voc dev. vs group | Insulation + to Earth (MΩ) | Insulation – to Earth (MΩ) | Insulation + to – (MΩ) | Polarity | Operating Voltage (V) | String Current (A) | Result | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
Strings — Pass | [6 empty] | Strings — Incomplete
Strings — Fail
Officer Name | [6 empty] | Signature

## DC INV 02
DC STRING TEST — INV 02
INVERTER DETAILS
Inverter No. |  |  |  | INV 02 |  |  | Inverter Location / Room
Make / Model | [6 empty] | Serial No.
Rated Capacity (kW) | [6 empty] | Date / Time
Tested By | [6 empty] | Weather / Irradiance (W/m²)
Total Strings Listed | [6 empty] | Total PV Modules
STRING TESTS — each string is entered ONCE (MPPT / string / module count are not repeated)
STRING DETAILS |  |  |  | NO-LOAD (before energising) | [5 empty] | ON-LOAD |  | RESULT
No. | MPPT | String | PV Modules | Voc (V) | Voc dev. vs group | Insulation + to Earth (MΩ) | Insulation – to Earth (MΩ) | Insulation + to – (MΩ) | Polarity | Operating Voltage (V) | String Current (A) | Result | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
Strings — Pass | [6 empty] | Strings — Incomplete
Strings — Fail
Officer Name | [6 empty] | Signature

## AC Output
AC OUTPUT TEST (grid no-load and inverter on-load)
AC SIDE READINGS — first row = grid side with inverters OFF, then each inverter ON-LOAD
Date | [5 empty] | Tested By
POINT |  |  | VOLTAGE L–N (V) |  |  | CURRENT (A) |  |  | POWER |  |  | RESULT
No. | Grid / Inverter & Room | Time | L1 | L2 | L3 | L1 | L2 | L3 | Active Power (kW) | PF | Freq (Hz) | Result | Remarks
1 | Grid side (no load)
2
3
4
5
6
7
8
9
10
11
12
Total plant AC power (kW)
Result checks every phase against the voltage window and the frequency against the tolerance set on “Equipment and Limits”. Leave unused phases blank for single-phase inverters.
Officer Name | [6 empty] | Signature

## AC Insulation and Earthing
AC INSULATION & EARTHING TEST
AC SIDE INSULATION RESISTANCE (MΩ) — one row per inverter / circuit (grid side and main panel can be added as extra rows)
Date |  |  |  |  | Test Voltage (V) |  |  |  |  | Tested By
No. | Inverter / Circuit | L1–L2 | L1–L3 | L2–L3 | L1–N | L2–N | L3–N | L1–E | L2–E | L3–E | N–E | Result | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
Single-phase: type N/A in the cells that do not apply. If the tester shows “>” or “OL”, type the highest number displayed.
EARTHING TEST
Rod No. | Location | Value (Ω) |  |  | Result |  | Remarks
1
2
3
4
5
6
7
8
Officer Name | [6 empty] | Signature

## Thermal Imaging
THERMAL IMAGING TEST
TEST CONDITIONS
Date |  |  |  | Ambient Temp (°C)
Irradiance (W/m²) |  |  |  | Tested By
SOLAR PANELS — CRITICAL / HOT PANELS
No. | Inverter / String | Panel Serial No. | Time | Temp (°C) | ΔT vs ambient (°C) | Result | Comment
1
2
3
4
5
6
7
8
9
10
INVERTERS
No. | Inverter / Room | Point Inspected | Time | Temp (°C) | ΔT vs ambient (°C) | Result | Comment
1
2
3
4
5
6
7
8
SWITCHGEAR PANEL — BREAKERS
No. | Breaker (Main / Inverter) | Rating / Ref | Time | IN Temp (°C) | OUT Temp (°C) | Result | Comment
1 | Main Breaker
2
3
4
5
6
7
8
9
Result = Fail when the hottest reading is more than the ΔT limit (see “Equipment and Limits”) above ambient. Attach thermal images to the report separately.
Officer Name |  |  | Signature

## Battery
BATTERY TEST (hybrid / battery-backed systems)
BATTERY SYSTEM DETAILS
Battery Brand & Model |  |  |  | No. of Modules / Racks
Battery Type |  |  |  | No. of Battery Strings
Bank Capacity (kWh) |  |  |  | BMS Model
Nominal Voltage (V) |  |  |  | Date / Tested By
BATTERY MODULE / STRING VOLTAGE & INSULATION
No. | Module / Rack No. | String No. | Nominal Voltage (V) | Measured Voltage (V) | Insulation (MΩ) | Status | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
BATTERY PROTECTION & BMS SETTINGS
No. | Parameter | Set / Measured | Standard / Ref | Result | Remarks
1 | Over Voltage Protection (V)
2 | Under Voltage Protection (V)
3 | Over Current Protection (A)
4 | Over Temperature Protection (°C)
5 | Under Temperature Protection (°C)
6 | Cell Balancing Function Test
7 | SOC Display Accuracy
8 | BMS Communication / Monitoring Test
9 | Battery Emergency Shutdown Test
CHARGE / DISCHARGE / BACKUP TEST
Test |  | Start Time | End Time | Start / End SOC (%) | Start / End Voltage (V) | Current (A) | Duration (min) | Remarks
Charge Test
Discharge Test
Backup / Off-Grid Test (grid failure simulation)
Officer Name |  |  |  | Signature

## Protection and Grid
PROTECTION & GRID SETTINGS VERIFICATION
No. | Parameter | Set / Measured Value | Standard / Reference | Result | Remarks
1 | Over Voltage Protection Trip (V)
2 | Under Voltage Protection Trip (V)
3 | Over Frequency Protection Trip (Hz)
4 | Under Frequency Protection Trip (Hz)
5 | Anti-Islanding Protection Test
6 | Reconnection Time Delay (s)
7 | Export Power Limit Setting (kW / %)
8 | RCD / ELCB Rated Trip Current (mA)
9 | RCD / ELCB Trip Test Result
10 | Earth Fault Protection Test
11 | Remote Shutdown / Emergency Stop Test
12 | Communication Module (WiFi / 4G / RS485) Test
13 | Monitoring Portal Registration
14 | Inverter Firmware Version(s)
Verified By |  |  | Date

## Punch List
PUNCH LIST / SNAG LIST
No. | Date Raised | Location / Inverter | Issue Description | Category | Raised By | Corrective Action | Responsible | Target Date | Status | Closed Date
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18

## Sign-Off
FINAL COMMISSIONING SIGN-OFF
Overall Commissioning Result
Commissioned Date
Commissioned Officer Name |  |  | Signature
SIGN-OFF
Role | Name | Company | Signature | Date
Commissioning Engineer
QA / QC Engineer
Client Representative / Consultant
Site Safety Officer
HANDOVER CHECKLIST
Item |  |  | Status
As-built drawings provided
O&M manual provided
Warranty certificates provided
Spare parts list provided
O&M training conducted
Monitoring portal access provided
Test certificates / thermal images attached
COMMENTS